OREGON OCCUPATIONAL

SAFETY AND HEALTH STANDARDS

Oregon Administrative Rules, Chapter 437

DIVISION 3   (29 CFR 1926)

CONSTRUCTION

CONSTRUCTION

Subdivision F

Fire Protection and Prevention

Oregon Occupational Safety and Health Division  (Oregon OSHA)

Department of Consumer and Business Services

Salem, Oregon 97301-3882

AO 5-2012

The Oregon Department of Consumer and Business Services adopted these rules pursuant to ORS

654.025(2).

The Secretary of State Designated OAR Chapter 437 as the “Oregon Occupational Safety and Health Code.”

Six general subject areas within this code are designated as “Divisions.”

- Division 1  General Administrative Rules

- Division 2  General Occupational Safety and Health Rules

- Division 3  Construction

- Division 4  Agriculture

- Division 5  Maritime Activities

- Division 7  Forest Activities

- Oregon Revised Statutes (ORS)  654 The Oregon Safe Employment Act (OSEAct)

Oregon-initiated rules in this division of the Oregon Occupational Safety and Health Code are numbered in a uniform system developed by the Secretary of State.  This system does not number the rules in sequence (001, 002, 003, etc.).  Omitted numbers may be assigned to new rules at the time of their adoption.

Oregon-initiated rules are arranged in the following Basic Codification Structure adopted by the Secretary of

State for Oregon Administrative Rules (OAR):

Chapter	Division	Rule	Section	Subsection	 Paragraphs

437	003	1760	(1)	(a)	(A)(i)(I)

The majority of Oregon OSHA codes are adopted by reference from the Code of Federal Regulations (CFR),

and are arranged in the following basic federal numbering system:

Chapter	Division	Part	Subpart	Section	 Paragraphs

(Subdivision)

437	003	1926	M	.502	(a)

The terms “subdivision” and “subpart” are synonymous within OAR 437, Oregon Occupational Safety and

Health Code.

To obtain an order form or copies of these codes, address:

Department of Consumer & Business Services

Oregon Occupational Safety & Health Division (Oregon OSHA)

350 Winter St. NE, Room 430

Salem, OR 97301-3882

Or call the Oregon OSHA Resource Library at 503-378-3272

The rules referenced in this division are available for viewing in the Office of the Secretary of State, Administrative Rules and Office Document Section, Oregon State Archives Building, Salem, Oregon 97310,

or the Central Office, Oregon Occupational Safety and Health Division of the Department of Consumer and Business Services, Room 430, 350 Winter St. NE Salem, OR 97301-3882.  Please visit our web site at:  www.orosha.org

TABLE OF CONTENTS

1926.150	Fire protection	F-1

1926.151	Fire prevention	F-5

1926.152	Flammable liquids	F-7

1926.153	Liquified petroleum gas  (LP-Gas)	F-12

1926.154	Temporary heating devices	F-18

1926.155	Definitions applicable to this subdivision	F-19

OAR 437, DIVISION 3

CONSTRUCTION

SUBDIVISION  F  –   FIRE PROTECTION AND PREVENTION

437-003-0001  Adoption by Reference.  In addition to, and not in lieu of, any other safety and health codes contained in OAR Chapter 437, the Department adopts by reference the following federal regulations printed as part of the Code of Federal Regulations, in the Federal Register:

(6) Subdivision F – Fire Protection and Prevention.

(a) 29 CFR 1926.150 Fire protection, published 4/6/79, FR vol. 44, p. 20940.

(b) 29 CFR 1926.151 Fire prevention, published 7/11/86, FR vol. 51, p. 25318.

(c) 29 CFR 1926.152 Flammable liquids, published 3/26/12, FR vol. 77, no. 58, p. 17574.

(d) 29 CFR 1926.153 Liquefied petroleum gas (LP-Gas), published 6/30/93, FR vol. 58, no. 124, p. 35170.

(e) 29 CFR 1926.154 Temporary heating devices, published 4/6/79, FR vol. 44, p. 20940.

(f) 29 CFR 1926.155 Definitions applicable to this subpart, published 3/26/12, FR vol. 77, no. 58, p. 17574.

These standards are available at the Oregon Occupational Safety and Health Division, Oregon Department of Consumer and Business Services, and the United States Government Printing Office.

Stat. Auth.:  ORS 654.025(2) and 656.726(4).

Stats. Implemented:  ORS 654.001 through 654.295.

Hist:	APD Admin. Order 5-1989, f. 3/31/89, ef. 5/1/89 (temp).

APD Admin. Order 8-1989, f. 7/7/89, ef. 7/7/89 (perm).

APD Admin. Order 14-1989, f. 7/20/89, ef. 8/1/89 (temp).

APD Admin. Order 15-1989, f. 9/13/89, ef. 9/13/89 (perm).

APD Admin. Order 16-1989 (temp), f. 9/13/89, ef. 9/13/89.

OR-OSHA Admin. Order 2-1989, f. 10/17/89, ef. 10/17/89.

OR-OSHA Admin. Order 3-1990, f. 1/19/90, ef. 1/19/90 (temp).

OR-OSHA Admin. Order 7-1990, f. 3/2/90, ef. 3/2/90 (perm).

OR-OSHA Admin. Order 8-1990, f. 3/30/90, ef. 3/30/90.

OR-OSHA Admin. Order 13-1990, f. 6/28/90, ef. 8/1/90 (temp).

OR-OSHA Admin. Order 19-1990, f. 8/31/90, ef. 8/31/90 (perm).

OR-OSHA Admin. Order 27-1990, f. 12/12/90, ef. 2/1/91.

OR-OSHA Admin. Order 6-1991, f. 3/18/91, ef. 4/15/91.

OR-OSHA Admin. Order 7-1991, f. 4/25/91, ef. 4/25/91.

OR-OSHA Admin. Order 15-1991, f. 12/13/91, ef. 12/13/91.

OR-OSHA Admin. Order 16-1991, f. 12/16/91, ef. 1/1/92.

OR-OSHA Admin. Order 6-1992, f. 5/18/92, ef. 5/18/92.

OR-OSHA Admin. Order 11-1992, f. 10/9/92, ef. 10/9/92.

OR-OSHA Admin. Order 1-1993, f. 1/22/93, ef. 1/22/93.

OR-OSHA Admin. Order 16-1993, f. 11/1/93, ef. 11/1/93 (Lead).

OR-OSHA Admin. Order 1-1994, f. 4/27/94, ef. 4/27/94.

OR-OSHA Admin. Order 4-1994, f. 8/4/94, ef. 8/4/94 (HazCom).

OR-OSHA Admin. Order 6-1994, f. 9/30/94, ef. 9/30/94.

OR-OSHA Admin. Order 1-1995, f. 1/19/95, ef. 1/19/95 (DOT markings, placards & labels).

OR-OSHA Admin. Order 3-1995, f. 2/22/95, ef. 2/22/95 (Haz Waste).

OR-OSHA Admin. Order 4-1995, f. 3/29/95, ef. 3/29/95 (Asbestos).

OR-OSHA Admin. Order 5-1995, f. 4/6/95, ef. 4/6/95 (HazCom).

OR-OSHA Admin. Order 6-1995, f. 4/18/95, ef. 6/1/95 (Fall Protection).

OR-OSHA Admin. Order 8-1995, f. 8/25/95, ef. 8/25/95 (Asbestos).

OR-OSHA Admin. Order 5-1996, f. 11/29/96, ef. 11/29/96.

OR-OSHA Admin. Order 6-1996, f. 11/29/96, ef. 11/29/96.

OR-OSHA Admin. Order 2-1997, f. 3/12/97, ef. 3/12/97.

OR-OSHA Admin. Order 4-1997, f. 4/2/97, ef. 4/2/97.

OR-OSHA Admin. Order 6-1997, f. 5/2/97, ef. 5/2/97.

OR-OSHA Admin. Order 7-1997, f. 9/15/97, ef. 9/15/97 (Fall Protection).

OR-OSHA Admin. Order 8-1997, f. 11/14/97, e. 11/14/97 (Methylene Chloride).

OR-OSHA Admin. Order 1-1998, f. 2/13/98, e. 2/13/98 (Methylene Chloride).

OR-OSHA Admin. Order 3-1998, f. 7/7/98, ef. 7/7/98 (Respiratory Protection).

OR-OSHA Admin. Order 6-1998, f. 10/15/98, ef. 10/15/98 (Slings 3/H).

OR-OSHA Admin. Order 7-1998, f. 12/28/98, ef. 12/28/98 (Asbestos).

OR-OSHA Admin. Order 1-1999, f. 3/22/99, e. 3/22/99 (Methylene Chloride).

OR-OSHA Admin. Order 4-1999, f. 4/30/99, ef. 4/30/99.

OR-OSHA Admin. Order 6-1999, f. 5/26/99, ef. 5/26/99.

OR-OSHA Admin. Order 3-2000, f. 2/8/00, ef. 2/8/00.

OR-OSHA Admin. Order 3-2001, f. 2/5/01, ef. 2/5/01 (Fall Protection/Oregon Exceptions).

OR-OSHA Admin. Order 3-2002, f. 4/15/02, ef. 4/18/02 (Steel Erection).

OR-OSHA Admin. Order 5-2002, f. 6/28/02, ef. 10/1/03 (GFCI 3/K).

OR-OSHA Admin. Order 6-2002, f. 7/19/02, ef. 7/19/02 (Fall Protection/Steel Erection).

OR-OSHA Admin. Order 1-2003, f. 1/30/03, ef. 4/30/03 (3/Q Masonry Wall Bracing).

OR-OSHA Admin. Order 2-2003, f. 1/30/03, ef. 1/30/03 (3/G).

OR-OSHA Admin. Order 7-2003, f. 12/5/03, ef. 12/5/03 (3/O).

OR-OSHA Admin. Order 8-2003, f. 12/30/03, ef. 1/1/04 (3/R).

OR-OSHA Admin. Order 1-2005, f. 4/12/05, ef. 4/12/05 (3/D and 3/Z).

OR-OSHA Admin. Order 2-2006, f. 4/28/06, ef. 4/28/06 (3/R).

OR-OSHA Admin. Order 4-2006, f. 7/24/06, ef. 7/24/06.

OR-OSHA Admin. Order 5-2006, f. 8/7/06, ef. 1/1/07.

OR-OSHA Admin. Order 6-2006, f. 8/30/06, ef. 8/30/06.

OR-OSHA Admin. Order 10-2006, f. 11/30/06, ef. 11/30/06.

OR-OSHA Admin. Order 6-2007, f. 9/26/07, ef. 9/26/07 (3/O).

OR-OSHA Admin. Order 5-2008, f. 5/1/08, ef. 5/15/08 (PPE).

OR-OSHA Admin. Order 5-2009, f. 5/29/09, ef. 5/29/09.

OR-OSHA Admin. Order 3-2010, f. 6/10/10, ef. 6/15/10.

OR-OSHA Admin. Order 1-2011, f. 2/9/11, ef. 2/9/11.

OR-OSHA Admin. Order 4-2011, f. 12/8/11, ef. 12/8/11.

OR-OSHA Admin. Order 5-2011, f. 12/8/11, ef. 7/1/12.

OR-OSHA Admin. Order 1-2012, f. 4/10/12, ef. 4/10/12.

OR-OSHA Admin. Order 5-2012, f. 9/25/12, ef. 9/25/12.

OR-OSHA Admin. Order 1-2013, f. 2/14/13, ef. 2/14/13.

OR-OSHA Admin. Order 2-2013, f. 2/15/13, ef. 4/1/13.

OR-OSHA Admin. Order 4-2013, f. 7/19/13, ef. 7/19/13.

OR-OSHA Admin. Order 5-2013, f. 9/13/13, ef. 9/13/13.

OR-OSHA Admin. Order 6-2013, f. 10/9/13, ef. 10/9/13.

OR-OSHA Admin. Order 7-2013, f. 12/12/13, ef. 12/12/13.

OR-OSHA Admin. Order 6-2014, f. 10/28/14, ef. 5/1/15.

OR-OSHA Admin. Order 7-2014, f. 11/7/14, ef. 11/9/14.

SUBDIVISION  F

FIRE  PROTECTION  AND  PREVENTION

Authority:  Section 107 of the Contract Work Hours and Safety Standards Act (40 U.S.C. 3704); Sections 4, 6, and 8 of the Occupational Safety and Health Act of 1970 (29 U.S.C. 653, 655, 657); Secretary of Labor's Order No. 12-71 (36 FR 8754), 8-76 (41 FR 25059), 9-83 (48 FR 35736),1-90 (55 FR 9033), 6-96 (62 FR 111), 3-2000 (62 FR 50017), 5-2002 (67 FR 650008), 5-2007 (72 FR 31159), 4-2010 (75 FR 55355), or 1-2012 (77 FR 3912), as applicable; and 29 CFR part 1911.

§1926.150  Fire Protection.

- General requirements.

  - The employer shall be responsible for the development of a fire protection program to be followed throughout all phases of the construction and demolition work, and he shall provide for the firefighting equipment as specified in this subpart.  As fire hazards occur, there shall be no delay in providing the necessary equipment.

  - Access to all available firefighting equipment shall be maintained at all times.

  - All firefighting equipment, provided by the employer, shall be conspicuously located.

  - All firefighting equipment shall be periodically inspected and maintained in operating condition.  Defective equipment shall be immediately replaced.

  - As warranted by the project, the employer shall provide a trained and equipped firefighting organization (Fire Brigade) to assure adequate protection to life.

- Water supply.

  - A temporary or permanent water supply, of sufficient volume, duration, and pressure, required to properly operate the firefighting equipment shall be made available as soon as combustible materials accumulate.

  - Where underground water mains are to be provided, they shall be installed, completed, and made available for use as soon as practicable.

- Portable firefighting equipment.

  - Fire extinguishers and small hose lines.

    - A fire extinguisher, rated not less than 2A, shall be provided for each 3,000 square feet of the protected building area, or major fraction thereof.  Travel distance from any point of the protected area to the nearest fire extinguisher shall not exceed 100 feet.

    - One 55-gallon open drum of water with two fire pails may be substituted for a fire extinguisher having a 2A rating.

    - A 1/2-inch diameter garden-type hose line, not to exceed 100 feet in length and equipped with a nozzle, may be substituted for a 2A-rated fire extinguisher, providing it is capable of discharging a minimum of 5 gallons per minute with a minimum hose stream range of 30 feet horizontally.  The garden-type hose lines shall be mounted on conventional racks or reels.  The number and location of hose racks or reels shall be such that at least one hose stream can be applied to all points in the area.

    - One or more fire extinguishers, rated not less than 2A, shall be provided on each floor.  In multistory buildings, at least one fire extinguisher shall be located adjacent to stairway.

    - Extinguishers and water drums, subject to freezing, shall be protected from freezing.

    - A fire extinguisher, rated not less than 10B, shall be provided within 50 feet of wherever more than 5 gallons of flammable or combustible liquids or 5 pounds of flammable gas are being used on the jobsite.  This requirement does not apply to the integral fuel tanks of motor vehicles.

    - Carbon tetrachloride and other toxic vaporizing liquid fire extinguishers are prohibited.

    - Portable fire extinguishers shall be inspected periodically and maintained in accordance with Maintenance and Use of Portable Fire Extinguishers, NFPA No. 10A-1970.

    - Fire extinguishers which have been listed or approved by a nationally recognized testing laboratory, shall be used to meet the requirements of this subpart.

    - Table F-1 may be used as a guide for selecting the appropriate portable fire extinguishers.

  - Fire hose and connections.

    - One hundred feet, or less, of 1-1/2-inch hose, with a nozzle capable of dis- charging water at 25 gallons or more per minute, may be substituted for a fire extinguisher rated not more than 2A in the designated area provided that the hose line can reach all points in the area.

    - If fire hose connections are not compatible with local firefighting equipment, the contractor shall provide adapters, or equivalent, to permit connections.

    - During demolition involving combustible materials, charged hose lines, supplied by hydrants, water tank trucks with pumps, or equivalent, shall be made available.

- Fixed firefighting equipment.

  - Sprinkler protection.

    - If the facility being constructed includes the installation of automatic sprinkler protection, the installation shall closely follow the construction and be placed in service as soon as applicable laws permit following completion of each story.

    - During demolition or alterations, existing automatic sprinkler installations shall be retained in service as long as reasonable.  The operation of sprinkler control valves shall be permitted only by properly authorized persons.  Modification of sprinkler systems to permit alterations or additional demolition should be expedited so that the automatic protection may be returned to service as quickly as possible.  Sprinkler control valves shall be checked daily at close of work to ascertain that the protection is in service.

  - Standpipes.  In all structures in which standpipes are required, or where standpipes exist in structures being altered, they shall be brought up as soon as applicable laws permit, and shall be maintained as construction progresses in such a manner that they are always ready for fire protection use.  The standpipes shall be provided with Siamese fire department connections on the outside of the structure, at the street level, which shall be conspicuously marked.  There shall be at least one standard hose outlet at each floor.

- Fire alarm devices.

  - An alarm system, e.g., telephone system, siren, etc., shall be established by the employer whereby employees on the site and the local fire department can be alerted for an emergency.

  - The alarm code and reporting instructions shall be conspicuously posted at phones and at employee entrances.

- Fire cutoffs.

  - Fire walls and exit stairways, required for the completed buildings, shall be given construction priority.  Fire doors, with automatic closing devices, shall be hung on openings as soon as practicable.

  - Fire cutoffs shall be retained in buildings undergoing alterations or demolition until operations necessitate their removal.

Stat. Auth.:  ORS 654.025(2) and 656.726(4).

Stats. Implemented:  ORS 654.001 through 654.295.

Hist:	APD Admin. Order 8-1989, f. 7/7/89, ef. 7/7/89.

§1926.151  Fire Prevention.

- Ignition hazards.

  - Electrical wiring and equipment for light, heat, or power purposes shall be installed in compliance with the requirements of Subpart K of this part.

  - Internal combustion engine powered equipment shall be so located that the exhausts are well away from combustible materials.  When the exhausts are piped to outside the building under construction, a clearance of at least 6 inches shall be maintained between such piping and combustible material.

  - Smoking shall be prohibited at or in the vicinity of operations which constitute a fire hazard, and shall be conspicuously posted: “No Smoking or Open Flame.”

  - Portable battery powered lighting equipment, used in connection with the storage, handling, or use of flammable gases or liquids, shall be of the type approved for the hazardous locations.

  - The nozzle of air, inert gas, and steam lines or hoses, when used in the cleaning or ventilation of tanks and vessels that contain hazardous concentrations of flammable gases or vapors, shall be bonded to the tank or vessel shell.  Bonding devices shall not be attached or detached in hazardous concentrations of flammable gases or vapors.

- Temporary buildings.

  - No temporary building shall be erected where it will adversely affect any means of exit.

  - Temporary buildings, when located within another building or structure, shall be of either noncombustible construction or of combustible construction having a fire resistance of not less than 1 hour.

  - Temporary buildings, located other than inside another building and not used for the storage, handling, or use of flammable or combustible liquids, flammable gases, explo- sives, or blasting agents, or similar hazardous occupancies, shall be located at a dis- tance of not less than 10 feet from another building or structure.  Groups of temporary buildings, not exceeding 2,000 square feet in aggregate, shall, for the purposes of this part, be considered a single temporary building.

- Open yard storage.

  - Combustible materials shall be piled with due regard to the stability of piles and in no case higher than 20 feet.

  - Driveways between and around combustible storage piles shall be at least 15 feet wide and maintained free from accumulation of rubbish, equipment, or other articles or materials.  Driveways shall be so spaced that a maximum grid system unit of 50 feet by 150 feet is produced.

  - The entire storage site shall be kept free from accumulation of unnecessary combus- tible materials.  Weeds and grass shall be kept down and a regular procedure provided for the periodic cleanup of the entire area.

  - When there is a danger of an underground fire, that land shall not be used for com- bustible or flammable storage.

  - Method of piling shall be solid wherever possible and in orderly and regular piles.  No combustible material shall be stored outdoors within 10 feet of a building or structure.

  - Portable fire extinguishing equipment, suitable for the fire hazard involved, shall be provided at convenient, conspicuously accessible locations in the yard area.  Portable fire extinguishers, rated not less than 2A, shall be placed so that maximum travel distance to the nearest unit shall not exceed 100 feet.

- Indoor storage.

  - Storage shall not obstruct, or adversely affect, means of exit.

  - All materials shall be stored, handled, and piled with due regard to their fire characteristics.

  - Noncompatible materials, which may create a fire hazard, shall be segregated by a barrier having a fire resistance of at least 1 hour.

  - Material shall be piled to minimize the spread of fire internally and to permit conven- ient access for firefighting.  Stable piling shall be maintained at all times.  Aisle space shall be maintained to safely accommodate the widest vehicle that may be used within the building for firefighting purposes.

  - Clearance of at least 36 inches shall be maintained between the top level of the stored material and the sprinkler deflectors.

  - Clearance shall be maintained around lights and heating units to prevent ignition of combustible materials.

  - A clearance of 24 inches shall be maintained around the path of travel of fire doors unless a barricade is provided, in which case no clearance is needed.  Material shall not be stored within 36 inches of a fire door opening.

(44 FR 8577, Feb. 9, 1979; 44 FR 20940, Apr. 6, 1979, as amended at 51 FR 25318, July 11, 1986)

Stat. Auth.:  ORS 654.025(2) and 656.726(4).

Stats. Implemented:  ORS 654.001 through 654.295.

Hist:	APD Admin. Order 8-1989, f. 7/7/89, ef. 7/7/89.

§1926.152  Flammable Liquids.

- General requirements.

  - Only approved containers and portable tanks shall be used for storage and handling of flammable liquids.  Approved safety cans or Department of Transportation approved containers shall be used for the handling and use of flammable liquids in quantities of 5 gallons or less, except that this shall not apply to those flammable liquid materials which are highly viscid (extremely hard to pour), which may be used and handled in original shipping containers.  For quantities of one gallon or less, the original container may be used, for storage, use and handling of flammable liquids.

  - Flammable liquids shall not be stored in areas used for exits, stairways, or normally used for the safe passage of people.

- Indoor storage of flammable liquids.

  - No more than 25 gallons of flammable liquids shall be stored in a room outside of an approved storage cabinet.  For storage of liquefied petroleum gas, see §1926.153.

  - Quantities of flammable liquid in excess of 25 gallons shall be stored in an acceptable or approved cabinet meeting the following requirements:

    - Acceptable wooden storage cabinets shall be constructed in the following manner, or equivalent: The bottom, sides, and top shall be constructed of an exterior grade of plywood at least 1 inch in thickness, which shall not break down or delaminate under standard fire test conditions.  All joints shall be rabbeted and shall be fastened in two directions with flathead wood screws.  When more than one door is used, there shall be a rabbeted overlap of not less than 1 inch.  Steel hinges shall be mounted in such a manner as to not lose their holding capacity due to loosening or burning out of the screws when subjected to fire.  Such cabinets shall be painted inside and out with fire retardant paint.

    - Approved metal storage cabinets will be acceptable.

    - Cabinets shall be labeled in conspicuous lettering, “Flammable – Keep Away from Open Flames”.

  - Not more than 60 gallons of Category 1, 2 and/or 3 flammable liquids or 120 gallons of Category 4 flammable liquids shall be stored in any one storage cabinet.  Not more than three such cabinets may be located in a single storage area.  Quantities in excess of this shall be stored in an inside storage room.

    - Inside storage rooms shall be constructed to meet the required fire-resistive rating for their use.  Such construction shall comply with the test specifications set forth in Standard Methods of Fire Test of Building Construction and Material, NFPA 251-1969.

    - Where an automatic extinguishing system is provided, the system shall be designed and installed in an approved manner.  Openings to other rooms or build- ings shall be provided with noncombustible liquid-tight raised sills or ramps at least 4 inches in height, or the floor in the storage area shall be at least 4 inches below the surrounding floor.  Openings shall be provided with approved self-closing fire doors.  The room shall be liquid-tight where the walls join the floor.  A permissible alternate to the sill or ramp is an open-grated trench, inside of the room, which drains to a safe location.  Where other portions of the building or other buildings are exposed, windows shall be protected as set forth in the Standard for Fire Doors and Windows, NFPA No. 80-1970, for Class E or F openings.  Wood of at least 1-inch nominal thickness may be used for shelving, racks, dunnage, scuffboards, floor overlay, and similar installations.

    - Materials which will react with water and create a fire hazard shall not be stored in the same room with flammable liquids.

    - Storage in inside storage rooms shall comply with Table F-2 following:

| Table F-2 |  |  |  |
| --- | --- | --- | --- |
| Fire protection provided | Fire resistance | Maximum size | Total allowable quantities gals./sq. ft./floor area |
| Yes No Yes No | 2 hrs. 2 hrs. 1 hr. 1 hr. | 500 sq. ft. 500 sq. ft. 150 sq. ft. 150 sq. ft. | 10 4 5 2 |
| Note: Fire protection system shall be sprinkler, water spray, carbon dioxide or other system approved by a nationally recognized testing laboratory for this purpose. |  |  |  |

    - Electrical wiring and equipment located in inside storage rooms shall be approved for Class I, Division 1, Hazardous Locations.  For definition of Class I, Division 1, Hazardous Locations, see §1926.449.

    - Every inside storage room shall be provided with either a gravity or a mechanical exhausting system.  Such system shall commence not more than 12 inches above the floor and be designed to provide for a complete change of air within the room at least 6 times per hour.  If a mechanical exhausting system is used, it shall be controlled by a switch located outside of the door.  The ventilating equipment and any lighting fixtures shall be operated by the same switch.  An electric pilot light shall be installed adjacent to the switch if Category 1, 2 or 3 flammable liquids are dispensed within the room.  Where gravity ventilation is provided, the fresh air intake, as well as the exhausting outlet from the room, shall be on the exterior of the building in which the room is located.

    - In every inside storage room there shall be maintained one clear aisle at least 3 feet wide.  Containers over 30 gallons capacity shall not be stacked one upon the other.

    - Flammable liquids in excess of that permitted in inside storage rooms shall be stored outside of buildings in accordance with paragraph (c) of this section.

  - “Quantity.”  The quantity of flammable liquids kept in the vicinity of spraying operations shall be the minimum required for operations and should ordinarily not exceed a supply for 1 day or one shift.  Bulk storage of portable containers of flammable or combustible liquids shall be in a separate, constructed building detached from other important buildings or cut off in a standard manner.

- Storage outside buildings.

  - Storage of containers (not more than 60 gallons each) shall not exceed 1,100 gallons in any one pile or area.  Piles or groups of containers shall be separated by a 5-foot clearance.  Piles or groups of containers shall not be nearer than 20 feet to a building.

  - Within 200 feet of each pile of containers, there shall be a 12-foot-wide access way to permit approach of fire control apparatus.

  - The storage area shall be graded in a manner to divert possible spills away from buildings or other exposures, or shall be surrounded by a curb or earth dike at least 12 inches high.  When curbs or dikes are used, provisions shall be made for draining off accumulations of ground or rain water, or spills of flammable liquids.  Drains shall terminate at a safe location and shall be accessible to operation under fire conditions.

  - Outdoor portable tank storage:

    - Portable tanks shall not be nearer than 20 feet from any building.  Two or more portable tanks, grouped together, having a combined capacity in excess of 2,200 gallons, shall be separated by a 5-foot-clear area.  Individual portable tanks exceeding 1,100 gallons shall be separated by a 5-foot-clear area.

    - Within 200 feet of each portable tank, there shall be a 12-foot-wide access way to permit approach of fire control apparatus.

  - Storage areas shall be kept free of weeds, debris, and other combustible material not necessary to the storage.

  - Portable tanks, not exceeding 660 gallons, shall be provided with emergency venting and other devices, as required by chapters III and IV of NFPA 30-1969, The Flammable and Combustible Liquids Code.

  - Portable tanks, in excess of 660 gallons, shall have emergency venting and other devices, as required by chapters II and III of The Flammable and Combustible Liquids Code, NFPA 30-1969.

- Fire control for flammable liquid storage.

  - At least one portable fire extinguisher, having a rating of not less than 20-B units, shall be located outside of, but not more than 10 feet from, the door opening into any room used for storage of more than 60 gallons of flammable liquids.

  - At least one portable fire extinguisher having a rating of not less than 20-B units shall be located not less than 25 feet, nor more than 75 feet, from any flammable liquid storage area located outside.

  - When sprinklers are provided, they shall be installed in accordance with the Standard for the Installation of Sprinkler Systems, NFPA 13-1969.

  - At least one portable fire extinguisher having a rating of not less than 20-B:C units shall be provided on all tank trucks or other vehicles used for transporting and/or dispensing flammable liquids.

- Dispensing liquids.

  - Areas in which flammable liquids are transferred at one time, in quantities greater than 5 gallons from one tank or container to another tank or container, shall be separated from other operations by 25-feet distance or by construction having a fire resistance of at least 1 hour.  Drainage or other means shall be provided to control spills.  Adequate natural or mechanical ventilation shall be provided to maintain the concentration of flammable vapor at or below 10 percent of the lower flammable limit.

  - Transfer of Category 1, 2 or 3 flammable liquids from one container to another shall be done only when containers are electrically interconnected (bonded).

  - Flammable liquids shall be drawn from or transferred into vessels, containers, or tanks within a building or outside only through a closed piping system, from safety cans, by means of a device drawing through the top, or from a container, or portable tanks, by gravity or pump, through an approved self-closing valve.  Transferring by means of air pressure on the container or portable tanks is prohibited.

  - The dispensing units shall be protected against collision damage.

  - Dispensing devices and nozzles for Category 1, 2 or 3 flammable liquids shall be of an approved type.

- Handling liquids at point of final use.

  - Category 1, 2 or 3 flammable liquids shall be kept in closed containers when not actually in use.

  - Leakage or spillage of Category 1, 2 or 3 flammable liquids shall be disposed of promptly and safely.

  - Flammable liquids may be used only where there are no open flames or other sources of ignition within 50 feet of the operation, unless conditions warrant greater clearance.

- Service and refueling areas.

  - Flammable liquids shall be stored in approved closed containers, in tanks located underground, or in aboveground portable tanks.

  - The tank trucks shall comply with the requirements covered in the Standard for Tank Vehicles for Flammable and Combustible Liquids, NFPA No. 385-1966.

  - The dispensing hose shall be an approved type.

  - The dispensing nozzle shall be an approved automatic-closing type without a latch-open device.

  - Underground tanks shall not be abandoned.

  - Clearly identified and easily accessible switch(es) shall be provided at a location remote from dispensing devices to shut off the power to all dispensing devices in the event of an emergency.

    - Heating equipment of an approved type may be installed in the lubrication or service area where there is no dispensing or transferring of Category 1, 2 or 3 flammable liquids, provided the bottom of the heating unit is at least 18 inches above the floor and is protected from physical damage.

    - Heating equipment installed in lubrication or service areas, where Category 1, 2 or 3 flammable liquids are dispensed, shall be of an approved type for garages, and shall be installed at least 8 feet above the floor.

  - There shall be no smoking or open flames in the areas used for fueling, servicing fuel systems for internal combustion engines, receiving or dispensing of flammable liquids.

  - Conspicuous and legible signs prohibiting smoking shall be posted.

  - The motors of all equipment being fueled shall be shut off during the fueling operation.

  - Each service or fueling area shall be provided with at least one fire extinguisher having a rating of not less than 20-B:C located so that an extinguisher will be within 75 feet of each pump, dispenser, underground fill pipe opening, and lubrication or service area.

(44 FR 8577, Feb. 9, 1979; 44 FR 20940, Apr. 6, 1979, as amended at 51 FR 25318, July 11, 1986)

Stat. Auth.:  ORS 654.025(2) and 656.726(4).

Stats. Implemented:  ORS 654.001 through 654.295.

Hist:	APD Admin. Order 8-1989, f. 7/7/89, ef. 7/7/89.

OR-OSHA Admin. Order 4-1999, f. 4/30/99, ef. 4/30/99.

OR-OSHA Admin. Order 3-2000, f. 2/8/00, ef. 2/8/00.

OR-OSHA Admin. Order 5-2012, f. 9/25/12, ef. 9/25/12.

§1926.153  Liquified Petroleum Gas (LP-Gas).

- Approval of equipment and systems.

  - Each system shall have containers, valves, connectors, manifold valve assemblies, and regulators of an approved type.

  - All cylinders shall meet the Department of Transportation specification identification requirements published in 49 CFR Part 178, Shipping Container Specifications.

  - Definition.  As used in this section, “Containers” – All vessels, such as tanks, cylinders, or drums, used for transportation or storing liquefied petroleum gases.

- Welding on LP-Gas containers.  Welding is prohibited on containers.

- Container valves and container accessories.

  - Valves, fittings, and accessories connected directly to the container, including primary shut off valves, shall have a rated working pressure of at least 250 p.s.i.g. and shall be of material and design suitable for LP-Gas service.

  - Connections to containers, except safety relief connections, liquid level gauging devices, and plugged openings, shall have shutoff valves located as close to the container as practicable.

- Safety devices.

  - Every container and every vaporizer shall be provided with one or more approved safety relief valves or devices.  These valves shall be arranged to afford free vent to the outer air with discharge not less than 5 feet horizontally away from any opening into a building which is below such discharge.

  - Shutoff valves shall not be installed between the safety relief device and the container, or the equipment or piping to which the safety relief device is connected, except that a shutoff valve may be used where the arrangement of this valve is such that full required capacity flow through the safety relief device is always afforded.

  - Container safety relief devices and regulator relief vents shall be located not less than 5 feet in any direction from air openings into sealed combustion system appliances or mechanical ventilation air intakes.

- Dispensing.

  - Filling of fuel containers for trucks or motor vehicles from bulk storage containers shall be performed not less than 10 feet from the nearest masonry-walled building, or not less than 25 feet from the nearest building or other construction and, in any event, not less than 25 feet from any building opening.

  - Filling of portable containers or containers mounted on skids from storage containers shall be performed not less than 50 feet from the nearest building.

- Requirements for appliances.

  - LP-Gas consuming appliances shall be approved types.

  - Any appliance that was originally manufactured for operation with a gaseous fuel other than LP-Gas, and is in good condition, may be used with LP-Gas only after it is properly converted, adapted, and tested for performance with LP-Gas before the appliance is placed in use.

- Containers and regulating equipment installed outside of buildings or structures.  Containers shall be upright upon firm foundations or otherwise firmly secured.  The possible effect on the outlet piping of settling shall be guarded against by a flexible connection or special fitting.

- Containers and equipment used inside of buildings or structures.

  - When operational requirements make portable use of containers necessary, and their location outside of buildings or structures is impracticable, containers and equipment shall be permitted to be used inside of buildings or structures in accordance with paragraphs (h)(2) through (11) of this section.

  - “Containers in use” means connected for use.

  - Systems utilizing containers having a water capacity greater than 2-1/2 pounds (nominal 1 pound LP-Gas capacity) shall be equipped with excess flow valves.  Such excess flow valves shall be either integral with the container valves or in the connections to the container valve outlets.

  - Regulators shall be either directly connected to the container valves or to manifolds connected to the container valves.  The regulator shall be suitable for use with LP-Gas.  Manifolds and fittings connecting containers to pressure regulator inlets shall be designed for at least 250 p.s.i.g. service pressure.

  - Valves on containers having water capacity greater than 50 pounds (nominal 20 pounds LP-Gas capacity) shall be protected from damage while in use or storage.

  - Aluminum piping or tubing shall not be used.

  - Hose shall be designed for a working pressure of at least 250 p.s.i.g.  Design, construction, and performance of hose, and hose connections shall have their suitability determined by listing by a nationally recognized testing agency.  The hose length shall be as short as practicable.  Hoses shall be long enough to permit compliance with spacing provisions of paragraphs (h)(1) through (13) of this section, without kinking or straining, or causing hose to be so close to a burner as to be damaged by heat.

  - Portable heaters, including salamanders, shall be equipped with an approved automatic device to shut off the flow of gas to the main burner, and pilot if used, in the event of flame failure.  Such heaters, having inputs above 50,000 B.t.u. per hour, shall be equipped with either a pilot, which must be lighted and proved before the main burner can be turned on, or an electrical ignition system.

Note:  The provisions of this subparagraph do not apply to portable heaters under 7,500 B.t.u. per hour input when used with containers having a maximum water capacity of 2-1/2 pounds.

  - Container valves, connectors, regulators, manifolds, piping, and tubing shall not be used as structural supports for heaters.

  - Containers, regulating equipment, manifolds, pipe, tubing, and hose shall be located to minimize exposure to high temperatures or physical damage.

  - Containers having a water capacity greater than 2-1/2 pounds (nominal 1 pound LP-Gas capacity) connected for use shall stand on a firm and substantially level surface and, when necessary, shall be secured in an upright position.

  - The maximum water capacity of individual containers shall be 245 pounds (nominal 100 pounds LP-Gas capacity).

  - For temporary heating, heaters (other than integral heater-container units) shall be located at least 6 feet from any LP-Gas container.  This shall not prohibit the use of heaters specifically designed for attachment to the container or to a supporting standard, provided they are designed and installed so as to prevent direct or radiant heat application from the heater onto the containers.  Blower and radiant type heaters shall not be directed toward any LP-Gas container within 20 feet.

  - If two or more heater-container units, of either the integral or nonintegral type, are located in an unpartitioned area on the same floor, the container or containers of each unit shall be separated from the container or containers of any other unit by at least 20 feet.

  - When heaters are connected to containers for use in an unpartitioned area on the same floor, the total water capacity of containers, manifolded together for connection to a heater or heaters, shall not be greater than 735 pounds (nominal 300 pounds LP-Gas capacity).  Such manifolds shall be separated by at least 20 feet.

  - Storage of containers awaiting use shall be in accordance with paragraphs (j) and (k) of this section.

- Multiple container systems.

  - Valves in the assembly of multiple container systems shall be arranged so that replacement of containers can be made without shutting off the flow of gas in the system.  This provision is not to be construed as requiring an automatic change-over device.

  - Heaters shall be equipped with an approved regulator in the supply line between the fuel cylinder and the heater unit.  Cylinder connectors shall be provided with an excess flow valve to minimize the flow of gas in the event the fuel line becomes ruptured.

  - Regulators and low-pressure relief devices shall be rigidly attached to the cylinder valves, cylinders, supporting standards, the building walls, or otherwise rigidly secured, and shall be so installed or protected from the elements.

- Storage of LPG containers.  Storage of LPG within buildings is prohibited.

- Storage outside of buildings.

  - Storage outside of buildings, for containers awaiting use, shall be located from the nearest building or group of buildings, in accordance with the following:

| ###### Table F-3 |  |
| --- | --- |
| Quantity of LP Gas Stored: | Distance (feet) |
| 500 lbs. or less ........................................................................ 501 to 6,000 lbs. ...................................................................... 6,001 to 10,000 lbs. ................................................................. Over 10,000 lbs. ...................................................................... | 0 10 20 25 |

  - Containers shall be in a suitable ventilated enclosure or otherwise protected against tampering.

- Fire protection.  Storage locations shall be provided with at least one approved portable fire extinguisher having a rating of not less than 20-B:C.

- Systems utilizing containers other than DOT containers.

  - Application.  This paragraph applies specifically to systems utilizing storage containers other than those constructed in accordance with DOT specifications.  Paragraph (b) of this section applies to this paragraph unless otherwise noted in paragraph (b) of this section.

  - Design pressure and classification of storage containers.  Storage containers shall be designed and classified in accordance with Table F-31.

| Table F-31 |  |  |  |
| --- | --- | --- | --- |
| Container type | For gases with vapor press. Not to exceed lb. per sq. in. gage at 100º F. (37.8º C.) | Minimum design pressure of container, lb. per sq. in. gage |  |
|  |  | 1949 and earlier editions of ASME Code (Par. U-68, U-69) | 1949 edition of ASME Code (Par. U-200, U-201); 1950, 1952, 1956, 1959, 1962, 1965, and 1968 (Division 1) editions of ASME Code; All editions of API-ASME Code3 |
| 80 1 100 125 150 175 200 2 | 80 1 100 125 150 175 215 | 80 1 100 125 150 175 200 | 100 1 125 156 187 219 250 |
| 1 New storage containers of the 80 type have not been authorized since Dec. 31, 1947. 2 Container type may be increased by increments of 25. The minimum design pressure of containers shall per 100 percent of the container type designation when constructed under 1949 or earlier editions of the ASME Code (Par. U-68 and U-69). The minimum design pressure of containers shall be 125 percent of the container type designation when constructed under: (1) the 1949 ASME Code (Par. U-200 and U-201), (2) 1950, 1952, 1956, 1959, 1962, 1965, and 1968 (Division 1) editions of the ASME Code, and (3) all editions of the API-ASME Code. 3 Construction of containers under the API-ASME Code is not authorized after July 1, 1961. |  |  |  |

  - Containers with foundations attached (portable or semiportable b containers with suitable steel “runners” or “skids” and popularly known in the industry as “skid tanks”) shall be designed, installed, and used in accordance with these rules subject to the following provisions:

    - If they are to be used at a given general location for a temporary period not to exceed 6 months they need not have fire-resisting foundations or saddles but shall have adequate ferrous metal supports.

    - They shall not be located with the outside bottom of the container shell more than 5 feet (1.52 m) above the surface of the ground unless fire-resisting supports are provided.

    - The bottom of the skids shall not be less than 2 inches (5.08 cm) or more than 12 inches (30.48 cm) below the outside bottom of the container shell.

    - Flanges, nozzles, valves, fittings, and the like, having communication with the interior of the container, shall be protected against physical damage.

    - When not permanently located on fire-resisting foundations, piping connections shall be sufficiently flexible to minimize the possibility of breakage or leakage of connections if the container settles, moves, or is otherwise displaced.

    - Skids, or lugs for attachment of skids, shall be secured to the container in accordance with the code or rules under which the container is designed and built (with a minimum factor of safety of four) to withstand loading in any direction equal to four times the weight of the container and attachments when filled to the maximum permissible loaded weight.

  - Field welding where necessary shall be made only on saddle plates or brackets which were applied by the manufacturer of the tank.

- When LP-Gas and one or more other gases are stored or used in the same area, the containers shall be marked to identify their content.  Marking shall be in compliance with American National Standard Z48.1-1954, “Method of Marking Portable Compressed Gas Containers To Identify the Material Contained.”

- Damage from vehicles.  When damage to LP-Gas systems from vehicular traffic is a possibility, precautions against such damage shall be taken.

Stat. Auth.:  ORS 654.025(2) and 656.726(4).

Stats. Implemented:  ORS 654.001 through 654.295.

Hist:	APD Admin. Order 8-1989, f. 7/7/89, ef. 7/7/89.

OR-OSHA Admin. Order 3-2000, f. 2/8/00, ef. 2/8/00.

§1926.154  Temporary Heating Devices.

- Ventilation.

  - Fresh air shall be supplied in sufficient quantities to maintain the health and safety of workmen.  Where natural means of fresh air supply is inadequate, mechanical ventilation shall be provided.

  - When heaters are used in confined spaces, special care shall be taken to provide sufficient ventilation in order to ensure proper combustion, maintain the health and safety of workers, and limit temperature rise in the area.

- Clearance and mounting.

  - Temporary heating devices shall be installed to provide clearance to combustible material not less than the amount shown in Table F-4.

  - Temporary heating devices, which are listed for installation with lesser clearances than specified in Table F-4, may be installed in accordance with their approval.

| Table F-4 |  |  |  |
| --- | --- | --- | --- |
| ###### Heating appliances | Minimum clearance, (inches) |  |  |
|  | Sides | Rear | Chimney connector |
| Room heater, circulating type ......................... Room heater, radiant type .............................. | 12 36 | 12 36 | 18 18 |

  - Heaters not suitable for use on wood floors shall not be set directly upon them or other combustible materials.  When such heaters are used, they shall rest on suitable heat insulating material or at least 1-inch concrete, or equivalent.  The insulating material shall extend beyond the heater 2 feet or more in all directions.

  - Heaters used in the vicinity of combustible tarpaulins, canvas, or similar coverings shall be located at least 10 feet from the coverings.  The coverings shall be securely fastened to prevent ignition or upsetting of the heater due to wind action on the covering or other material.

- Stability.  Heaters, when in use, shall be set horizontally level, unless otherwise permitted by the manufacturer’s markings.

- Solid fuel salamanders.  Solid fuel salamanders are prohibited in buildings and on scaffolds.

- Oil-fired heaters.

  - Flammable liquid-fired heaters shall be equipped with a primary safety control to stop the flow of fuel in the event of flame failure.  Barometric or gravity oil feed shall not be considered a primary safety control.

  - Heaters designed for barometric or gravity oil feed shall be used only with the integral tanks.

  - (Reserved)

  - Heaters specifically designed and approved for use with separate supply tanks may be directly connected for gravity feed, or an automatic pump, from a supply tank.

Stat. Auth.:  ORS 654.025(2) and 656.726(4).

Stats. Implemented:  ORS 654.001 through 654.295.

Hist:	APD Admin. Order 8-1989, f. 7/7/89, ef. 7/7/89.

§1926.155  Definitions Applicable to this Subdivision.

- Approved, for the purpose of this subpart, means equipment that has been listed or approved by a nationally recognized testing laboratory such as Factory Mutual Engineering Corp., or Underwriters' Laboratories, Inc., or Federal agencies such as Bureau of Mines, or U.S. Coast Guard, which issue approvals for such equipment.

- Closed container means a container so sealed by means of a lid or other device that neither liquid nor vapor will escape from it at ordinary temperatures.

- Reserved.

- Combustion means any chemical process that involves oxidation sufficient to produce light or heat.

- Fire brigade means an organized group of employees that are knowledgeable, trained, and skilled in the safe evacuation of employees during emergency situations and in assisting in fire fighting operations.

- Fire resistance means so resistant to fire that, for specified time and under conditions of a standard heat intensity, it will not fail structurally and will not permit the side away from the fire to become hotter than a specified temperature.  For purposes of this part, fire resistance shall be determined by the Standard Methods of Fire Tests of Building Construction and Materials, NFPA 251-1969.

- Flammable means capable of being easily ignited, burning intensely, or having a rapid rate of flame spread.

- Flammable liquid means any liquid having a vapor pressure not exceeding 40 pounds per square inch (absolute) at 100 degrees F (37.8 degrees C) and having a flashpoint at or below 199.4 degrees F (93 degrees C).  Flammable liquids are divided into four categories as follows:

  - Category 1 shall include liquids having flashpoints below 73.4 degrees F (23 degrees C) and having a boiling point at or below 95 degrees F (35 degrees C).

  - Category 2 shall include liquids having flashpoints below 73.4 degrees F (23 degrees C) and having a boiling point above 95 degrees F (35 degrees C).

  - Category 3 shall include liquids having flashpoints at or above 73.4 degrees F (23 degrees C) and at or below 140 degrees F (60 degrees C).

  - Category 4 shall include liquids having flashpoints above 140 degrees F (60 degrees C) and at or below 199.4 degrees F (93 degrees C).

- Flash point of the liquid means the temperature at which it gives off vapor sufficient to form an ignitable mixture with the air near the surface of the liquid or within the vessel used as determined by appropriate test procedure and apparatus as specified below.

  - The flashpoint of liquids having a viscosity less than 45 Saybolt Universal Second(s) at 100 degrees F (37.8 degrees C) and a flashpoint below 175 degrees F (79.4 degrees C) shall be determined in accordance with the Standard Method of Test for Flash Point by the Tag Closed Tester, ASTM D-56-69 (incorporated by reference; See § 1926.6), or an equivalent method as defined by § 1910.1200 Appendix B.

  - The flashpoints of liquids having a viscosity of 45 Saybolt Universal Second(s) or more at 175 degrees F (79.4 degrees C) or higher shall be determined in accordance with the Standard Method of Test for Flash Point by the Pensky Martens Closed Tester, ASTM D-93-69 (incorporated by reference; See § 1926.6), or an equivalent method as defined by § 1910.1200 Appendix B.

- Liquefied petroleum gases, LPG and LP Gas mean and include any material which is composed predominantly of any of the following hydrocarbons, or mixtures of them, such as propane, propylene, butane (normal butane or iso-butane), and butylenes.

- Portable tank means a closed container having a liquid capacity more than 60 U.S. gallons, and not intended for fixed installation.

- Safety can means an approved closed container, of not more than 5 gallons capacity, having a flash-arresting screen, spring-closing lid and spout cover and so designed that it will safely relieve internal pressure when subjected to fire exposure.

- Vapor pressure means the pressure, measured in pounds per square inch (absolute), exerted by a volatile liquid as determined by the "Standard Method of Test for Vapor Pressure of Petroleum Products (Reid Method)." (ASTM D-323-58).

Stat. Auth.:  ORS 654.025(2) and 656.726(4).

Stats. Implemented:  ORS 654.001 through 654.295.

Hist:	APD Admin. Order 8-1989, f. 7/7/89, ef. 7/7/89.

OR-OSHA Admin. Order 5-2012, f. 9/25/12, ef. 9/25/12.